## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2020-12-01
System Name: | Ranbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 118 |  | 12.4 | 25 | 0.016 | 0.019
2 | 118 |  | 12.4 | 25 | 0.015 | 0.016
3 | 119 |  | 12.6 | 25 | 0.015 | 0.018
4 | 120 |  | 13.4 | 25 | 0.015 | 0.015
5 | 120 |  | 13.2 | 25 | 0.015 | 0.016
6 | 120 |  | 13.3 | 25 | 0.015 | 0.015
7 | 122 |  | 13.3 | 25 | 0.015 | 0.019
8 | 124 |  | 13.3 | 25 | 0.015 | 0.015
9 | 125 |  | 13.3 | 25 | 0.015 | 0.015
10 | 126 |  | 13.2 | 25 | 0.015 | 0.015
11 | 127 |  | 12.8 | 25 | 0.013 | 0.013
12 | 127 |  | 12.8 | 25 | 0.015 | 0.015
13 | 128 |  | 12.9 | 25 | 0.015 | 0.015
14 | 129 |  | 12.3 | 25 | 0.015 | 0.015
15 | 127 |  | 10.5 | 25 | 0.02 | 0.02
16 | 128 |  | 11.01 | 25 | 0.015 | 0.015
17 | 133 |  | 11.4 | 25 | 0.017 | 0.021
18 | 108 |  | 7.5 | 25 | 0.03 | 0.35
19 | 112 |  | 12 | 25 | 0.019 | 0.033
20 | 112 |  | 12.8 | 25 | 0.03 | 0.5
21 | offfline |  | offline | 25 | offline | offline
22 | offfline |  | offline | 25 | offline | offline
23 | offfline |  | offline | 25 | offline | offline
24 | offfline |  | offline | 25 | offline | offline
25 | offfline |  | offline | 25 | offline | offline
26 | offfline |  | offline | 25 | offline | offline
27 | offfline |  | offline | 25 | offline | offline
28 | offfline |  | offline | 25 | offline | offline
29 | 111 |  | 10.1 | 25 | 0.02 | 0.05
30 | 112 |  | 11.3 | 25 | 0.017 | 0.02
31 | 113 |  | 12.5 | 25 | 0.017 | 0.02
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:1/6/20
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 )954-9941 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Ranbow Water District |  | ID#: 41 00839 |  | Month/Year: | 2020-12-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.73 | 210.79 | 153.8767 | 14.8 | 6.78 | 24.6597 | YES | 389
2 | 0.7 | 211.99 | 148.393 | 14.7 | 6.77 | 24.6485 | YES | 386.8
3 | 0.72 | 210.25 | 151.38 | 14.8 | 6.76 | 24.4483 | YES | 390
4 | 0.72 | 211.44 | 152.2368 | 14.7 | 6.77 | 24.7051 | YES | 387.8
5 | 0.72 | 210.68 | 151.6896 | 14.7 | 6.77 | 24.7051 | YES | 389.2
6 | 0.69 | 211.23 | 145.7487 | 14.6 | 6.78 | 24.8787 | YES | 388.2
7 | 0.69 | 211.06 | 145.6314 | 14.6 | 6.78 | 24.8787 | YES | 388.5
8 | 0.68 | 210.14 | 142.8952 | 14.6 | 6.78 | 24.8502 | YES | 390.2
9 | 0.69 | 210.36 | 145.1484 | 14.6 | 6.79 | 24.9716 | YES | 389.8
10 | 0.71 | 209.82 | 148.9722 | 14.6 | 6.78 | 24.9358 | YES | 390.8
11 | 0.7 | 213.26 | 149.282 | 14.5 | 6.78 | 25.075 | YES | 384.5
12 | 0.71 | 212.71 | 151.0241 | 14.5 | 6.78 | 25.1037 | YES | 385.5
13 | 0.69 | 212.54 | 146.6526 | 14.5 | 6.78 | 25.0462 | YES | 385.8
14 | 0.71 | 211.23 | 149.9733 | 14.5 | 6.79 | 25.1975 | YES | 388.2
15 | 0.62 | 213.65 | 132.463 | 14.6 | 6.79 | 24.772 | YES | 383.8
16 | 0.71 | 213.43 | 151.5353 | 14.5 | 6.78 | 25.1037 | YES | 384.2
17 | 0.38 | 213.26 | 81.0388 | 14.2 | 6.81 | 24.9409 | YES | 384.5
18 | 0.47 | 169.42 | 79.6274 | 14.4 | 6.79 | 24.6788 | YES | 484
19 | 0.62 | 167.62 | 103.9244 | 13.9 | 6.86 | 26.6485 | YES | 489.2
20 | 0.57 | 168.79 | 96.2103 | 13.7 | 6.82 | 26.4572 | YES | 485.8
21 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
22 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
23 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
24 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
25 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
26 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
27 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
28 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
29 | 0.55 | 169.07 | 92.9885 | 14.8 | 6.79 | 24.246 | YES | 485
30 | 0.62 | 165.65 | 102.703 | 14.7 | 6.79 | 24.6062 | YES | 495
31 | 0.64 | 164 | 104.96 | 13.9 | 6.74 | 25.5426 | YES | 500
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2